## Slide 1: RNG Gas Quality
Western Gas Measurement Short Course 2026

## Slide 2: What is RNG
What is RNG
  Renewable Natural Gas (RNG) is defined as a pipeline-compatible gaseous fuel derived from biogenic or other renewable sources that has lower life cycle carbon dioxide equivalent (CO2e) emissions than geologic natural gas
What is Biogas
  Gas produced from the anaerobic decomposition of organic material
What is Biomethane
  Biogas that has been conditioned or upgraded to comply with this Rule’s gas quality specifications
Notes: Toda I will Speaking to you about RNG and RNG gas quality
I will be going over the pipeline gas quality specifications which apply to all gas in our pipeline
And then I will speak to you regarding the rule 45 gas quality specifications which apply solely to RNG
I will go over the Trigger levels and action levels as specificized in rule 45
And lastly I will speak you a little about hydrogen and how we are planning on testing for it.

## Slide 3: Where Does RNG Come From?
Landfill
As organic waste like food scraps and paper break down in landfills, it produces methane. Capturing and cleaning methane can turn it into RNG
Wastewater Treatment Plants
When wastewater is treated at wastewater treatment plants, organic matter breaks down and produces methane. This methane is captured and processed into RNG.
Food Waste (Organic Waste)
When household or commercial food scraps, yard waste and other biodegradable materials break down in controlled environments, like anaerobic digesters, they produce methane, which can be converted into RNG.
Agriculture Waste
Manure and other agriculture byproducts, like crop residues, can be processed to produce methane through anaerobic digestion. This methane is then upgraded to RNG.
Notes: Toda I will Speaking to you about RNG and RNG gas quality
I will be going over the pipeline gas quality specifications which apply to all gas in our pipeline
And then I will speak to you regarding the rule 45 gas quality specifications which apply solely to RNG
I will go over the Trigger levels and action levels as specificized in rule 45
And lastly I will speak you a little about hydrogen and how we are planning on testing for it.

## Slide 4: Status of Renewable Gas Supplies
Rapidly expanding with CA leading in consumption
  99% of NG for vehicles is RNG in 2004
  84% nationwide
Still limited relative to potential demand
  Only a small fraction of total Nat Gas consumption in state
  Supply is constrained by feedstock availability, infrastructure and economics

## Slide 5: History of Biomethane Gas Quality Standards
Pre-2000’s when no/minimal standards existed
  Primarily used for on-site for electricity gen or thermal energy.
  Pipeline injection was rare
Early to mid 2000’s – Early pipeline injections
  Suffered from siloxane contaminations
  Corrosion
  Heating Value variability
  Oxygen intrustion
  Natural Gas Tarrif rules didn’t adequately address biogas-specific contaminants
Notes: Pre 200’s – high CO2 concentent moisture, h2s, siloxanes, nh3 and particulates.
Source :Biomethane in California Common Carrier Pipelines
Corrosion due to sulfur and moisture

## Slide 6: History of Biomethane Gas Quality Standards
Development of Utility- Specific Biomethane Standards (2013)
  Maximum allowable siloxanes
  TOS and individual Sulfur Specied
  Oxygen and Inert Limits
  Moisture and HC dew points
  Trace Contaminants
  Developed continuous monitoring of contaminants and composition
  Improved interconnection agreements
  Developed pre-injection testing requirements
Notes: Pre 200’s – high CO2 concentent moisture, h2s, siloxanes, nh3 and particulates.
Source :Biomethane in California Common Carrier Pipelines
Corrosion due to sulfur and moisture

## Slide 7: History of Biomethane Gas Quality Standards
Expansion of Utility- Specific Biomethane Standards (present)
  Updated toxicity criteria
  Revised list of constituents of concern and health protective levels
Notes: Pre 200’s – high CO2 concentent moisture, h2s, siloxanes, nh3 and particulates.
Source :Biomethane in California Common Carrier Pipelines
Corrosion due to sulfur and moisture

## Slide 8: History of Biomethane Gas Quality Standards Initial Standards based on California Air Resources Board (CARB) and Office of Environmental Health Hazard Assessment (OEHHA) Report: “Recommendations to the California Public Utilities Commission Regarding Health Protective Standards for the Injection of Biomethane into the Common Carrier Pipeline”, submitted in OIR 13-02-008 Constituents of Concern in Biogas: CARB and OEHHA did a comprehensive evaluation and identification of the constituents of concern in biogas focusing on the larger sources of biogas ‒ landfills, dairies, and sewage treatment plants Trigger and Action Levels: CARB staff recommended a risk management strategy1 wherein trigger levels and lower and upper action levels for potential cancer risk and total non-cancer hazard indexes are identified and evaluated to ensure that health protective levels are adequately maintained. CPUC DECISION 14-01-034 concluded that if biomethane meets the gas quality standards and testing protocols adopted in R. 13-02-008, then it may be injected into the California jurisdictional gas utility pipeline systems. File every 5 years review and update standards for constituents of concern In 2014, the CPUC D14-01-034 adopted concentration standards for 17 constituents of concern found in biomethane, and adopted certain monitoring, testing, reporting and recordkeeping protocols that the biomethane producers and gas utilities must comply with. Health Protective Constituents (HPC) Integrity Protective Constituents (IPC) OEHHA recommendation was issued in April 2023 to the CPUC. AL 6422-G (3/31/25) Revisions to Rule 45 in compliance with ordering paragraph 2 Decision 24-11-009 (10/1/24)
Notes: Toda I will Speaking to you about RNG and RNG gas quality
I will be going over the pipeline gas quality specifications which apply to all gas in our pipeline
And then I will speak to you regarding the rule 45 gas quality specifications which apply solely to RNG
I will go over the Trigger levels and action levels as specificized in rule 45
And lastly I will speak you a little about hydrogen and how we are planning on testing for it.

## Slide 9: RNG Gas Quality
  Pipeline Gas Quality Specifications : Rule 30
  Renewable Gas Interconnections : Rule 45
Rule 30 - May 31, 2019 |  | 
Heating Value (HHV) | 970~1150 | btu/SCF dry
Moisture Content or Water Content |  | 
 | <800 psig | 7 lb/mmSCF
 | >800 psig | Water dew point <20 F @ P
Hydrogen Sulfide | 0.25 grain of H2s (4 ppmV) | 
 | not contain any entrained hydrogen sulfide treatment chemical (solvent) or its by-products in the gas stream | 
Mercaptan Sulfur | 0.3 grain of mercaptans (5 ppmV) | 
Total Sulfur | 0.75 grain of total sulfur (12.6 ppmV) | 
 | This includes COS and CS2, hydrogen sulfide, mercaptans and mono, di and poly sulfides. | 
Carbon Dioxide | <3% | Vo%
Oxygen | <0.2% | Vo%
Inerts: | <4% | Vo%
 | carbon dioxide, nitrogen, oxygen and any other inert compound) | 
Hydrocarbons |  | 
 | 800 psig< | HC dew Point<45F @ delivery pressure or 400psig min
 | 800 psig> | HC dew Point<20F @ delivery pressure or 400psig min
Merchantability | dust, sand, dirt, gums, oils and other s | 
Hazardous Substances | not contain hazardous substance | 
Delivery Temperature: | 50~105 | °F
Interchangeability | Wobbe 1279~1385 | 
 |  | Lifting Index (IL)=<1.06
 |  | Flashback Index (IF)=<1.2
 |  | Yellow Tip Index (IY)>=0.8
Liquids | The gas shall contain no liquids at or immediately downstream of the receipt point | 
Notes: Toda I will Speaking to you about RNG and RNG gas quality
I will be going over the pipeline gas quality specifications which apply to all gas in our pipeline
And then I will speak to you regarding the rule 45 gas quality specifications which apply solely to RNG
I will go over the Trigger levels and action levels as specificized in rule 45
And lastly I will speak you a little about hydrogen and how we are planning on testing for it.

## Slide 10: On-going Gas Quality Monitoring and Enforcement
Continuous online gas analyzers will alarm and the controller will automatically shut off valve if not compliant.
Gas is rejected back to be recycled through the supplier’s process plant.
Shut off valve will be opened once alarm is cleared.
10
Supplier
Online Gas Analyzers
Controller
(PLC)
Recycle
Filter Sep
Meter
Pressure Regulator
& Shut off valve
Odorant
Utility Pipeline

## Slide 11: SoCalGas/SDG&E Rule 45

## Slide 12: Rule 45 - Health Protective Constituents (HPC) For Land Fill Gas
Chlorocarbons(*)
(*)
Biogas Consituents of Concern and Health Protective Levels for Biomethane: Supplement Report to OEHHA AB 1900 Biogas Recommendations

## Slide 13: Rule 45 - Health Protective Constituents (HPC) For Land Fill Gas
Fluorocarbons (as F)
Silicon Compounds (as Si)
Biogas Consituents of Concern and Health Protective Levels for Biomethane: Supplement Report to OEHHA AB 1900 Biogas Recommendations

## Slide 14: Rule 45 - Health Protective Constituents (HPC)
Sulfur Compounds (as S)
Biogas Consituents of Concern and Health Protective Levels for Biomethane: Supplement Report to OEHHA AB 1900 Biogas Recommendations
3rd Party Lab List

## Slide 15: Rule 45
Trigger Levels
Concentration of measured value of a consitutuent requiring periodic testing and analysis
Lower Action Level
Concentration of of measure value of a constituent requiring periodic testing and analysis
Required supplier shut-off if exceeded > 3 times in 12-month period
Upper Action Level
Concentration of measured value of a constituent requiring immediate shut-off of supplier
Notes: As we spoke about earlier with the rule 30 limits, rule 45 give separate ranges for action.
The trigger level gives the concentration of particular constituent that will trigger periodic testing and analysis
The lower action level is higher than the trigger level and serves the same purpose.
  The main difference is that if the producer exceeds this level 3 times in a 12-month period, will be shut in and they will have to fix the issue that causing the problem
The upper action level has an even greater concentration than the lower action limit
  If Producer exceeds this level, they are immediately shut in.
So since we were talking about the periodic testing we will go through the schedules.

## Slide 16: Testing Schedule
3rd Party Analysis
Review Results
Initial
24-Hour Startup
Periodic Testing
Periodic
Quarterly Testing
Annual Testing
Biennial Testing
4 Successful Tests
Fail
2 Successful Tests
Fail
Notes: Once the producer is ready to flow, they have a third party sample their gas and they submit their results and upon approval, We schedule a 24-hour test
During 24 hour test, all constituents are continuously monitored, and sample are sent to a third party lab upon completion.
If any of the Rule 30 constituents fail and can’t be corrected or any Rule 45 constituents goes above the upper action limit. The test is stopped, and the process begins again.
If everything is successful, the components are tested quarterly.

## Slide 17: Siloxanes
Integrity Risk:
  Premature failure of industrial equipment and appliances when siloxanes are burned/combusted and form a sand-like material (silica) deposits on equipment surfaces.
Research project:
  Appliance Study completed
  ASTM Standards for Siloxane analysis, now working on ILS (Interlaboratory study)
  Online siloxane analyzers
Updated Specifications for Siloxanes:
  Raised the Trigger level to 0.05 mg Si/m3
  Introduced the Upper Action Level of 0.3 mg Si/m3

## Slide 18: Ammonia
Integrity Risk/Concerns: Corrosion, NOx emissions,
Research project on ammonia impact on GC and end use completed by USC. Odor mask.
Updated Specifications for Ammonia
  Lowered the Trigger Level to 4 ppmv
  Introduced the Lower Action Level of 10 ppmv
  Introduced the Upper Action Level of 25 ppmv

## Slide 19: Mercury
Integrity Risk:
  Corrosion
Research:
  USC literature study – not available under NG pipeline conditions
  Currently working on identifying Action limits
Updated Specifications for Mercury
  0.01 ug/m3 for Cryogenic applications
  Annual progress updates to CPUC.

## Slide 20: Biologicals
Integrity Risk:
  Corrosion
Research/Study:
  GTI data shows no difference between RG and pipeline natural gas
Updated Levels for Biologicals:
  Test at pre-injection
  Propose: No biologicals >0.2 microns

## Slide 21: Pre-injection – Rule 45 - Biological
Renewable Gas must be commercially free of bacteria which cause corrosions (>0.2 microns)
During pre-injection testing, the Interconnector will test for total bacteria including but not limited to:
  Acid-producing Bacteria (APB),
  Sulfate-reducing Bacteria (SRB),
  Iron-oxidizing Bacteria (IOB)
  Using quantitative polymerase Chain Reaction (qPCR) method
If the total bacteria results are at or below 4x10^4/scf, then Renewable Gas may be injected into the Utility’s system.

## Slide 22: California Joint Utility Standard for Renewable Gas
Incorporation of Updated COCs
  Utilities plan to embed CARB’s updated COCs and testing rules into SRGI tariffs to enhance health safety standards.
Testing for Multiple Feedstocks
  Utilities propose testing all COCs for each feedstock type instead of only primary feedstock for better protection.
Phased Implementation Timelines
  Phased testing timelines range from three to eighteen months based on system size and resources to ensure smooth compliance.
Balancing Capacity and Compliance
  Phased approach avoids overloading labs and disrupting operations while achieving timely testing completion as recommended by CARB.

## Slide 23: California Joint Utility Standard for Renewable Gas
Developed by SoCalGas, PG&E, SDG&E and Southwest gas
  Replace inconsistent, utility-specific biomethane requirements
Applies to renewable gas producers seeking to inject into pipeline
  Landfills
  wastewater treatment plants
  dairy/livestock
  Organic and agricultural waste
  Bio-synthesis NG from organic feedstock